MEMO

TO: 		Billy Nunn, Plans Examiner

Michelle Robinson, Permit Technician

CC:		Shawn Ankeny, shawn@ankenyarchitecture.com

FROM:	Bobbi Clauson, Fire Inspector

DATE:		November 20, 2018

SUBJECT:	IWUIC Review 5370 W. Woodchuck Road

This office has reviewed the above area and determined the area fire hazard rating to be Moderate fire hazard.  Water supply is nonconforming.  With required defensible space of 30 feet structure shall be built using IR2 construction, as follows:

All construction features must be approved by the County Building Official prior to permitting.

Fire Department Access

- Driveways in excess of 150 feet shall be provided with turnaround.  Driveways in excess of 200 feet and less than 20 feet in width shall be provided with turnouts in addition to turnarounds.  Turnarounds shall have inside turning radii of not less than 30 feet and outside turning radii of not less than 45 feet.  Turnouts shall be all-weather road surface at least 10 feet wide and 30 feet long.  (IWUIC 403.2.5)

- Bridges shall be posted and designed for emergency vehicle load limits. (IWUIC 403.2.6)

Roof Covering, Etc.

- Roof covering shall have at least a Class B covering, per the building code requirement.  If the profile of the roof allows a space between the roof covering and roof decking, the space at the eave ends shall be fire-stopped to preclude entry of flames or embers. (IWUIC 505.2)

- Roof valleys, where provided, shall be not less than 0.019-inch corrosion-resistant metal installed over a minimum 36-inch-wide underlayment consisting of one layer of 72-pound mineral-surfaces, nonperforated cap sheet complying with ASTM D 3909 running the full length of the valley (IWUIC 506.2.1)

- Roof covering shall have at least a Class B covering. If the profile of the roof allows a space between the roof covering and roof decking, the space at the eave ends shall be fire-stopped to preclude entry of flames or embers. (IWUIC 505.2)

- Combustible eaves, fascias and soffits shall be enclosed with solid materials with a minimum thickness of 3 / 4 inch.  No exposed rafter tails shall be permitted unless constructed of heavy timber materials. (IWUIC 505.3)

- Gutters and downspouts shall be constructed of noncombustible material. (IWUIC 505.4)

Exterior Wall Protection

- Exterior walls of buildings or structures shall be constructed with materials approved for a minimum of 1-hour fire-resistance-rated construction on the exterior side or constructed with approved noncombustible materials, unless built of heavy timber or log wall construction.  Materials shall extend from the top of the foundation to the underside of the roof sheathing. (IWUIC 505.4)

Unenclosed Underfloor Protection

- Buildings or structures shall have all underfloor areas enclosed to the ground with exterior walls complying to IWUIC 505.5.  This may be exempted if the underside of all exposed floors and all exposed structural columns, beams and supporting walls are protected as required for exterior 1-hour fire-resistance-rated construction or heavy timber construction. (IWUIC 505.6)

Decks

- Unenclosed accessory structures attached to buildings with habitable spaces and projections, such as decks, shall be a minimum of 1-hour fire-resistance-rated construction, heavy timber construction or constructed of approved noncombustible materials or fire-resistance-rated construction, heavy timber construction or constructed of approved noncombustible materials or fire-retardant-treated wood identified for exterior use and meeting the requirements of the International Building Code. (IWUIC 505.7)

Windows/Glazing

- Exterior windows, window walls and glazed doors, windows within exterior doors, and skylights shall be tempered glass, multilayered glazed panels, glass block or have a fire-protection rating of not less than 20 minutes. (IWUIC 505.8)

Exterior Doors

- Exterior doors shall be approved noncombustible construction, solid core wood not less than 1 ¾ inches thick or have a fire protection rating of not less than 20 minutes.  Windows within doors and glazed doors shall be in accordance with IWUIC 505.8. (IWUIC 505.9)

Structure Ventilation

- Attic ventilation openings, soffit vents, foundation or underfloor vents or other ventilation openings in vertical exterior walls and vents through roofs shall not exceed 144 square inches each.  These vents shall be covered with noncombustible corrosion-resistant mesh with openings not to exceed ¼ inch or shall be designed and approved to prevent flame or ember penetration into the structure.  Attic ventilation openings shall not be located in soffits, in eave overhangs, between rafters at eaves, or in other overhang areas.  Gable end and dormer vents shall be located at least 10 feet from property lines and underfloor ventilation openings shall be located as close to grade as practical. (IWUIC 505.10) Teton County Ordinance allows for cold roof ventilation under very specific conditions.  Contact Fire Department for these requirements.

Accessory Structures

- Detached accessory structures located less than 50 feet from a building containing habitable space shall have exterior walls constructed with materials approved for a minimum of 1-hour fire-resistance-rated construction, heavy timber, log wall construction, or constructed with approved noncombustible material on the exterior side. (IWUIC 505.11) Exposed underfloor areas must be protected per IWUIC 505.11.1.

Miscellaneous

- All buildings shall have a permanently posted address, which shall be placed at each driveway entrance and be visible from both directions of travel along the road.   (IWUIC406.3)

- Firewood and combustible material shall not be stored in unenclosed spaces beneath buildings or structures, or on decks or under eaves, canopies or other projections or overhangs. (IWUIC 607.1)

- Chimneys serving fireplaces, barbecues, incinerators or decorative heating appliances in which solid or liquid fuel is used, shall be provided with a spark arrester.  Arrester shall be constructed of woven or welded wire screening of 12 gage wire having openings not exceeding ½ inch. (IWUIC 605.1)

- LP-gas containers shall be installed underground. (IWUIC 606.3; amended)

Required Defensible space is 30 feet  Trees must be kept greater than 10 feet from the structure and the crowns must be greater than 10 feet from crowns of adjacent trees.  Fire resistive vegetation is recommended within this area.  (IWUIC 603.2)

Above requirements shall be spelled out within construction documents for this project and shall require inspection when WUI requirements are being installed, constructed and/or assembled.  Final inspection will be required from this Department.

Should you have questions, please feel free to contact me at bclauson@tetoncountywy.gov or 307-733-4732.

# Comments

Name, email address from RP

Date

Insert fire hazard rating

Change if water conforms